## Slide 1: Psychrometrics
Wei FANG
NTU_BME and Global ATGS
National Taiwan University
the study of moist air and its thermodynamic properties
[ATGS 7140] Plant Factory – Theory and Practice
[ANISCI7047] Smart Production of Livestock

## Slide 2: Moist air
Moist air: air with water vapor
Dry air: air without water vapor
Moist air = dry air + water vapor
Dry air: mixed gas (N2: 80%, O2: 19%, Others: including CO2 400 ppm = 0.04% and else)

## Slide 3: Functions of moist air
As the heat source / sink
As the water source/ sink
As the N2 source / sink
As the O2 source / sink
As the source / sink of organic particles
As the source / sink of inorganic particles
others

## Slide 4: Applications of moist air
HVAC
Drying
(De)humidification
Evaporative cooling
  Pad and Fan
  Fogging
else

## Slide 5: Natural Ventilation
Summer
Winter
Forced Ventilation

## Slide 6: Pad and Fan system
Miss leading information in places other than extreme dry climate zone

## Slide 7: Fogging with fan

## Slide 8: Fogging Misting Spraying
Evaporative cooling

## Slide 9: fogging for comfort

## Slide 10: Temperature affects humidity
In general, it means
  Dry bulb Temperature
  affects
  Relative Humidity
But there are
  3 types of temperature and
  2 types of humidity

## Slide 11: Thermodynamic Properties of moist air
乾球溫度 dry bulb T
濕球溫度 wet bulb T
露點溫度 dew point T
相對溼度 relative humidity
絕對溼度 absolute humidity
  (濕度比humidity ratio)
比容 specific volume
熱焓 enthalpy
蒸汽壓vapor pressure
飽和蒸汽壓 saturated vapor pressure

## Slide 12: Daily variation of T and RH

## Slide 13: High T Low RH occurs at the same time
午夜
中午
午夜
T
RH

## Slide 14: Which one is wrong
High T
Low RH
High T, high RH
Low T
High RH

## Slide 15
Dry bulb Temperature, Tdb

## Slide 16: Relative Humidity, RH
Ratio of the vapor pressure (VP) of the moist air vs. saturated VP of the moist air at the same Tdb. in %
Saturated moist air means moist air at 100% RH
Air at higher temperature can absorb more water vapor
Moist air at same temperature, one with higher RH has less capacity left to absorb water vapor.

## Slide 17: Wet Bulb Temperature, Twb
Require device to measure RH
Without device,
RH can be derived from given Tdb and Twb

## Slide 18: Dry and Wet Bulb Temperature

## Slide 20: Tdb and Twb

## Slide 21
Tdb: 26 oC
Twb:17 oC
WBD: 9 oC
RH ≈ 36 %

## Slide 23: RH = f(Tdb and Twb)
Patm = 101.325 kPa = 1013.25 hPa

## Slide 24: RH = f(Tdb and Twb)

## Slide 25: Twb = f(Tdb, RH)

## Slide 26: Wet bulb depression, WBD
    WBD = Tdb – Twb
    Limit of the degree of temperature drop of the Evaporative cooling system

## Slide 27: WBD= Tdb – Twb = f(Tdb, RH) Web Bulb Depression

## Slide 28: Psychrometric properties
At given latitude (given Patm) and 2 independent properties, others can be derived.
Tdb、Twb  RH
Tdb、RH  Twb
Twb、RH  Tdb

## Slide 29: Psychrometric properties
3+1 T, 2 H and 2 P properties
  Tdb > Twb > Tdp (Dew point temperature)
  Tsat: Saturated T (Tdb at RH=100%)
  Relative Humidity (RH), Absolute Humidity (AH)
  Water vapor pressure (Pw)
  Saturated water vapor pressure (Pws, Pw at Tsat)

## Slide 30: 3+1 T
Tdb Tsat
Twb
Tdp: lowest temperature with no condensation occurred
  When surface T is lower than Tdp of the moist air, condensation will be occurred on the surface such as the eyeglass, cup, flower, leaves, etc.

## Slide 31: Portable digital T, RH measuring device

## Slide 32
Infra-red Dry Bulb Temperature
Measuring only the surface T
Not for surface T measurement
Need to know the emissivity of the surface of interest to correctly measure the surface temperature.

## Slide 33: Emissivity
Emissivity is a measure of a material’s radiating efficiency. An emissivity of 1.00 implies that the material is 100% efficient at radiating energy. An emissivity of 0.20 implies that the material radiates only 20% of that which it is capable of radiating. Black body ε= 1, Grey body ε < 1
Tables of emissivity values are only approximated values for real materials. A range of emissivity values is usually given for many materials whose emissivity can be affected by surface roughness or finish. Additionally, thin sheets of material such as plastics may be semi-transparent in the infrared and therefore have reduced emissivity

## Slide 34: Thermal Imager
http://us.fluke.com/usen/products/CategoryTI/
http://www.landinst.com/infrared/products/thermal_imaging/tp8_portable_imager.htm
http://www.landinst.com/infrared/products/thermal_imaging/guide_M4_thermal_imager.htm

## Slide 35: 2 H
Relative humidity (RH) in %
  Ratio of vapor pressure (mass) of moist air vs. saturated vapor pressure (mass) at same Tdb is called Relative Humidity (Degree of Saturation, DOS)
Absolute humidity (AH) in g/kg or kg/kg or g/m3 or kg/m3
  Mass (g or kg) of water vapor per kg or m3 of dry air

## Slide 36: AH
AH in g or kg/kg Dry Air (DA) divided by specific volume (SV) of DA is the AH in g or kg/m3 DA.
SV (m3/kg) is the inverse of air density (kg/m3)
At normal temperature range, mass of water vapor per 1 kg of dry air is 0 ~ 30 g
At same Tdb, air with higher RH has higher AH
At same RH, air with higher Tdb has higher AH

## Slide 37: How many PSY. related terms you have learned so far?
4 T, 2 H, 2 P
DOS
WBD
SV, Density

## Slide 38: Psychrometric Chart

## Slide 39: Psychrometric Chart

## Slide 43: Process: from one state to another

## Slide 46: 人體的溫溼度舒適帶

## Slide 47: Comfort zone of 3 animals
Dry bulb temperature
Productivity

## Slide 48
Psychart software

## Slide 49: RH = f(Tdb, Twb)

## Slide 50: WBD= Tdb – Twb = f(Tdb, RH)

## Slide 51: RH range for plant growth
Tdb, oC | RH too low (humidification required) | Proper RH | RH too high (dehumidification required)
15 | - | 50 % | 73
20 | 46 | 64 | 80
25 | 60 | 73 | 86
30 | 70 | 80 | 89

## Slide 53: unit conversion millibar to others

## Slide 54: VPD 1 millibar = 0.1 kPa
VPD too big (humidification or cooling required) | Proper VPD | VPD too small (dehumidification or heating required)
1.25 kPa | 0.85 kPa | < 0.45 kPa (Suitable for bacterial to survive) < 0.2 kPa (suitable for bacterial invasion)

## Slide 55: VPD = f(Tdb, RH)

## Slide 56: VPD is a better index for humidity control
Vapor Pressure Deficit

## Slide 57
https://cals.Arizona.edu/vpdcalc/
Saturated Vapor Pressure
Vapor Pressure Deficit
Humidity Deficit

## Slide 58: VPD is the driving force for the transpiration to occur. Proper VPD leads to proper transpiration, proper water/nutrient uptake and proper growth. VPD too high, stomata tends to close, no CO2 intake and no water/nutrient uptake. VPD too low, less transpiration occur, leads to less water/nutrients uptake, slow growth.

## Slide 59
Pws – Pw = VPD
Psychart 軟體

## Slide 60: VPD of GH_A during the night time
VPD too low at night.

## Slide 61: VPD of GH_B during the night time
VPD too low at night.

## Slide 62: Dehumidifier ON from 6 pm to 6 am
RH > 90% with dehumidifier OFF
Dehumidifier ON, RH at 80%
RH increase rapidly due to turn off of the dehumidifier, later decrease rapidly due to T increase inside the greenhouse after sunrise

## Slide 63: VPD difference due to ON/OFF of the dehumidifier
VPD > 0.45 kPa is safer compare with VPD < 0.2

## Slide 64: When outdoor RH is higher than indoor, ventilation can still be used to reduce the water content inside the greenhouse.
AHoutdoor
AHGH
RHGH
RHoutdoor

## Slide 65
Natural ventilation can also remove indoor water vapor when indoor AH is higher than outdoor AH
Notes: 即溫暖和潮濕的空氣大多比室外空氣輕
自然煙囪效應 氣流往上

## Slide 66: How many PSY. related terms you have learned so far?
4 T, 2 H, 2 P
DOS, WBD
SV, Density
VPDair, VPDairTdbwb, VPDair_leaf
HDair, HDairTdbwb, HDindoor_outdoor

## Slide 67: Tutorial for Psyc0226
Wei Fang, Ph.D., Professor
Dept. of Bio-Industrial Mechatronics Engineering
National Taiwan University
Software last updated: 2002/02/26

## Slide 68: Psyc0226
Allow alteration on atmospheric pressure
Provide handy PsyTables
  Totally 11 tables are available
Provide PsyCharts
  State calculation: besides AtmP, values of 2 independent states are required to calculate others
  Process calculation: find differences between 2 states
  More process calculation:
    Evaporative cooling
    Vapor pressure deficit on leaf

## Slide 69: Psyc0226 software
Tdb: dry bulb Temp.
RH : relative humidity
Twb: wet bulb Temp.
Tdp: dew point Temp.
AH : absolute humidity
H: enthalpy
SV : specific volume
Hfg: evaporated latent heat
DOS: degree of saturation
Pws: saturated water vapor pressure
Pw: water vapor pressure
Further illustration of the cell

## Slide 70: Red zone is the chart

## Slide 71: Two ways to set the atmospheric pressure

## Slide 72: 11 handy PsyTables

## Slide 73: User friendly 3-step design in PsyTable
1. Define the ranges
3. List the values
2. Set the intervals

## Slide 74: Table 1: Twb = f(Tdb, RH)
RH (50 – 100%)and Tdb (20 – 44 oC)
Twb

## Slide 75: Table 2: WBD = f(Tdb,RH)
WBD
Wet Bulb Depression is the limit of evaporative cooling methods.

## Slide 76: Table 3: RH = f(Tdb,Twb)
Twb (20 – 44 oC) and Tdb (20 – 44 oC)
RH

## Slide 77: Table 4: VPD of air, Table 10: AHD

## Slide 78: VPD=Pws@Tdb – Pw@Tdb AHD=Sat.AH@Tdb – Sat.AH@Tdp
VPD/AHD of air

## Slide 79: Table 5: VPD’ of air, Table 11: AHD’

## Slide 80: VPD’=Pw@Twb – Pw@Tdb AHD’=Sat.AH@Twb – Sat.AH@Tdp
VPD’/AHD’ of air

## Slide 81
6
7
Table 6: Tdp
Table 7: Tdp

## Slide 82: Table 8, 9: THI, Temperature Humidity Index
8
9

## Slide 83: Impact of T and RH on milk production of cows
THI >85, no recovery
Adapted from ASHRAE Fundamentals, 1999
75.73
79.96
63.7
65.05
72.32
68.47
63.39
76.68
90.09
87.09
88.06
64.31
64.65
82.49
86.01
82.09
82.36
84.21

## Slide 84: Milk production decline vs. Temperature-Humidity Index (THI)
Adapted from ASHRAE Fundamentals, 1999

## Slide 85
MP = f(HD74, HA80S)
MP = 21.48 – 0.051 * HD74 – 0.0099 * HA80S
where,
MP: milk production per cow per day (in kg/day/cow)
21.48: regular MP amount (in kg)
HD74: total hours of THI > 74 for previous 4 days
HA80S: square of total hours of THI > 80 for previous day
  Linvill and Pardue (1992)

## Slide 86: Iso-THI lines

## Slide 87: Table 10: AHD or HD
10

## Slide 88: Table 11: AHD’ or HD’
11

## Slide 89
VPD
AHD or HD
VPD’
AHD’ or HD’
Tdp

## Slide 90: Psycharts
Besides atmospheric pressure, values of 2 independent states are required to derive others
find differences between 2 states
Evaporative cooling process calculation
Vapor pressure deficit on leaf

## Slide 91: State Calculation

## Slide 92: Independent Properties (IP)
 | Twb | RH | Tdp | AH | SV | H | hfg | DOS | Pws | Pw
Tdb | IP | IP | IP | IP | IP | IP |  | IP |  | IP
Any pair of IP can be the given values to derive others.

## Slide 93: One click in Psychart window using left button of the mouse can define a state

## Slide 94: Process Calculation

## Slide 95: Use mouse to define 2 states
To define 2nd state, change from ‘Inactive’ to ‘Active’ first.
Click in the Psychart window at the selected state or click on the crosshair region to move along constant lines or curves.
Click on ‘Cal.’ to calculate the difference.

## Slide 96: Move along prefix lines or Curves
Constant Tdp, Pw, AH
Constant Twb
Constant RH
Constant Twb
Constant Tdp, Pw, AH
Constant RH
Constant Tdb
Constant Tdb

## Slide 97: Process: Move from 1 state to another
Sensible Heating (3->4)
Sensible Cooling (4->3)
Humidification (4->5)
Dehumidification (5->4)
Heating (3->5, 3->1)
Cooling (5->3, 1->3)
Air Mixing (1, 2->3)
Evaporative Cooling, Drying (1->2, 1->3)
Combination of above (1->2->3->4->5)

## Slide 98: Sensible heat gain

## Slide 99: Evaporative cooling
Limit: Outdoor WB Temperature
  Pad and Fan system
  Misting/Fogging with nozzle at one side of the wall
Limit: INDOOR WB Temperature
  Indoor Spraying/Misting/Fogging

## Slide 100: How to derive ΔT
ΔT = WBD of outdoor air x Pad Efficiency
T
T- ΔT

## Slide 101: Evaporative cooling of a pad
Enter T outdoor
Enter Pad efficiency
Derive others
2. Enter T after Pad
3. Derive others

## Slide 102: Click on “Draw” icon to visually see the outcome
WBD
ΔT

## Slide 103: Pad Efficiency vs. Air velocity (2 thickness of pad)
10 cm 厚
20 cm 厚

## Slide 104: ∆P vs. Air velocity (2 thickness of pad)
10 cm 厚
20 cm 厚

## Slide 105
Efficiency vs. Air velocity
Pressure drop vs. Air velocity

## Slide 106: Fan curves

## Slide 107: Vapor pressure deficit (VPD) of leaf
VPD
Enter Leaf temperature, then click on Draw icon.

## Slide 108: Shows the line/curves of the selected properties
Other handy features

## Slide 109
Shows the line/curves of the selected properties

## Slide 110: Zoom in Zoom out
Other handy features

## Slide 111: Unit label: to hide or not to hide the labels
Other handy features

## Slide 112: Centralize: allow the state that user chose to appear at the center of the chart
Other handy features

## Slide 113: Introducing LetsGrow
Wei FANG
NTU_BME and Global ATGS
National Taiwan University
A psychrometric software
[ATGS 7140] Plant Factory – Theory and Practice
[ANISCI7047] Smart Production of Livestock
https://gpe.letsgrow.com/psychro

## Slide 115
1 個大氣壓 = 海平面，海拔 0 m
假設氣孔內相對濕度為100%
此值>0 確保水汽也由氣孔出來

## Slide 116
作物範圍內微氣候
此值>0 確保水汽也散逸到溫室上方
= VPsat - VP

## Slide 117
詳細版本

## Slide 118
精簡版本

## Slide 119: 更多分析

## Slide 120
ExtraHeat = (Radiation*穿透率) – (U*dT)
=[500*0.8 - 0*(30-18)]*3600/1000 kJ/m2.h
∆Enthalpy=87.54-40.61=46.93 kJ/kg
Ventilation=ExtraHeat/∆Enthalpy
=400*3.6/46.93=30.69 kg/m2.h
ExtraHeat=[500*0.8 - 10*(30-18)]*3600/1000 kJ/m2.h
∆Enthalpy=87.54-40.61=46.93 kJ/kg
Ventilation=ExtraHeat/∆Enthalpy=(400-120)/46.93=21.48

## Slide 121
Value from Energy balance
AHD = 23.08 - 9.04 = 14.04 g/kg air
Moisture removed= 21.48 * 14.04 = 301.58 g/m2.h
Net Moisture balance = Moisture removed – Crop evaporation – fogging rate
= 301.58 – 50 - 100 = 151.58 g/ m2.h
Net Moisture balance = Moisture removed – Crop evaporation – fogging rate
= 301.58 – 50 - 0 = 251.58 g/ m2.h

## Slide 122
Moisture exhaust= AHD x Fan capacity x DensityinsideAir
= (23.08 – 9.04) x 10 x (26.43/23.08) = 160.778 g/m2.h
Air density
= (26.43/23.08) = 1.1451473
= (4.66/4.07) = 1.144963
Fan power = dP x 0.27778 / Efficiency
= 1000 x 0.27778 / 1 = 277.78 W
Fan power = dP x 0.27778 / Efficiency
= 100 x 0.27778 / 0.4 = 69.445 W
Elec. Consumption = Power * Area = 38.21*100 = 3821 W = 3821*3600/106 MJ/h = 3.821*3.6 = 13.7556 MJ/h

## Slide 123: Examples of using Psychart

## Slide 124: Properties
Under 1 ATM, the Tdb of moist air is 20 oC，RH is 50 %，what is the humidity ratio (absolute humidity, AH), degree of saturation (DOS), dew point temperature (Tdp), enthalpy (h), and wet bulb temperature (Twb)?

## Slide 125: Set the atmospheric pressure Patm

## Slide 128: Properties
Continue, What is the wet bulb depression (WBD) and vapor pressure deficit (VPD) ?

## Slide 129
WBD = Tdb – Twb = 20 – 13.79 = 6.21 deg. C

## Slide 130
VPD = Pws – Pw = 2.339 – 1.169 = 1.17 kPa

## Slide 131: Properties
Complete the following Tables
 | #1 | #2 | #3 | #4
Atmospheric pressure, kPa | 101.325 | 101.325 | 101.325 | 89.874
Dry-bulb T, deg.C | 20 | 20 | -10 | 20
Relative humidity, % | 50 | 80 | 50 | 50
Humidity ratio, kg/kg |  |  |  | 
Dew point T, deg.C |  |  |  | 
Wet bulb T, deg.C |  |  |  | 
Specific volume, m3/kg |  |  |  | 

## Slide 133
A bug was found in the software.
Twb should vary according to Patm.

## Slide 134: From one state to another state is called process

## Slide 135: Process
Determine the final state of moist air originally at 20 deg.C and 50 % relative humidity if 10 kJ are removed from 1.2 kg of the air.

## Slide 136: Answer to Q4
 T = q/(Ma*Cp)=(-10 kJ)/(1.2 kg*1.006 kJ/kg.K)= -8.28 K
The final dry bulb T will be 20 – 8.28 = 11.72 deg.C if this is a sensible heating process.
The dew point T of moist air at initial state = 9.15 deg.C
The final dry bulb T > the dew point T of initial state, this is a sensible cooling process.
 h =q/Ma = (-10 kJ)/(1.2 kg) = - 8.333 kJ/kg
The initial h = 38.5 kJ/kg
The final h = 38.545 – 8.333 = 30.212 kJ/kg
The initial dew point T = final dew point T.
Final state can be found based on final Tdb and Tdp, or Tdb and h, or Tdp and h

## Slide 137
State 2 was determined based on Tdb and H
H = 38.545 – 8.333 = 30.212 kJ/kg
Diff. of Tdp should be 0.

## Slide 138
State 2 was determined based on Tdb and Tdp
H = 8.591 kJ/kg which is a little bit off from 8.33 kJ/kg, also Diff. of AH should be 0.

## Slide 139: Process
Determine the final state of moist air originally at 20 deg.C and 50 % relative humidity if 20 kJ are removed from 1.2 kg of the air.

## Slide 140: Answer to Q5
 T = q/(Ma*Cp)=(-20kJ)/(1.2kg*1.006kJ/kg.K)= -16.56 K
The final T will be 20 – 16.56 = 3.44 deg.C if this is a sensible heating process.
The dew point T of moist air at initial state = 9.1 deg.C
The final dry bulb T < dew point at initial state, this is a cooling with condensation/dehumidification process.
The final relative humidity is 100 %.
 h =q/Ma = (-20 kJ)/(1.2 kg) = - 16.66 kJ/kg
The initial h = 38.545 kJ/kg
The final h = 38.545 – 16.66 = 21.885 kJ/kg

## Slide 141
State 2 can be determined based on RH and H,
however, this software does not provide this option. We need to use trial and error method on Tdb of state 2 to derive H = -16.66 kJ/kg..

## Slide 142: Process
Greenhouse in tropical and subtropical regions often encounter high humidity problem. For some floral industries, dehumidifier is used in the greenhouses. Assuming the night time Tdb and RH in a 3 m height 1000 m2 greenhouse before turn on the dehumidifier is 18 degree C, 91 % respectively. After turn on the dehumidifier for a while, the Tdb remain the same and RH drop to 80 %. How much water was removed from the moist air inside this greenhouse ?

## Slide 144: Answer to Q6
Before use
  Specific volume = 0.8404 m3/kg
  AH = 0.0117 kg vapor/kg dry air
After use
  AH = 0.0103 kg vapor/kg dry air
Difference in AH
  AH1 – AH2 = 0.0014 kg vapor/kg dry air
  Air volume 1000 x 3 = 3000 m3
  Air weight = 3000 / 0.8404 = 3569.7 kg
  Total water condensed = 3569.7 * 0.0014 = 4.997 kg

## Slide 145: Process
Air at 30 deg.C and 60% relative humidity in a growth chamber is cycled past the cooling coils and is returned back to the chamber at a temperature of 15 deg.C. Determine the psychrometric properties of the air after it is cooled, the sensible and latent heat removed, and the water vapor condensed per kg of dry air moved past the coils.

## Slide 146
Growth Chamber
30 deg.C
60 % relative humidity
Cooler
15 deg.C

## Slide 147
29.16 kJ/kg is the total heat removed, including the sensible heat and the latent heat.

## Slide 148
15.378 kJ/kg is the sensible heat removed

## Slide 149
13.782 kJ/kg is the latent heat removed
0.0054 kg/kg dry air is the amount of water removed
13.782/ 2428.4 = 0.00567 kg/kg dry air is the amount of water removed based on Hfg.

## Slide 150: Process
When ambient conditions are 35 deg.C and 25 % relative humidity, (a). determine the dry bulb temperature to which ventilation air could be cooled if drawn through an evaporative cooler with an efficiency of 75%. (b). Calculate how much water must be added to each cubic meter of the air drawn through the cooler. (c). Redo problem 7(a) with the ambient conditions at 35 deg.C and 80 % relative humidity.

## Slide 151: Answer to 8a
(a). At the given condition:
    Tdb = 35 deg.C
    RH = 25 % (Very dry weather)
Answer
    Twb = 20.15 deg.C
    WBD = 35 – 20.15 = 14.85 deg.C
    T = 0.75 * WBD = 11.13 deg.C
    Final T = 35 – 11.13 = 23.87 deg.C

## Slide 152
WBD

## Slide 153: Answer to 8c
(c). At the given condition:
    Tdb = 35 deg.C
    RH=80 % (Regular humid weather)
Answer
    Twb = 31.64 deg.C
    WBD = 35 – 31.64 = 3.36
    T = 0.75 * WBD = 2.52 deg.C
    Final T = 35 – 2.52 = 32.48 deg.C

## Slide 154
WBD

## Slide 155: Answer to 8b
(b). At initial conditions,
  Tdb = 35 deg.C
  RH = 25 %
Answer
  the specific volume is 0.8853 m3/kg, humidity ratio is 0.0088 kg/kg of dry air.
  At wet bulb of 20.15 and dry bulb of 23.87, the humidity ratio is 0.0132 kg/kg of dry air.
  A cubic meter of air will contain 1 m3/0.8853 m3/kg = 1.13 kg.
  The change of humidity ratio is 0.0132 – 0.0088 = 0.0044 kg/kg dry air.
  Thus, the total water gained by each cubic meter of outdoor air will be 1.13 kg * 0.0044 kg/kg = 0.005 kg.

## Slide 156
A small bug was found in the software. Both Twb should be the same.

## Slide 157: Process
A ventilation system for a calf nursery draws 1 m3/s of air from the nursery, exhausts 0.2 m3/s of the air to the outside, and replaces the exhausted air with fresh air. Air in the nursery is at 20 deg.C and 50 % relative humidity, and outdoor air is at 5 deg.C and 80 % relative humidity. Determine properties of the mixed air when it is returned to the nursery.

## Slide 158
Calf Nursery
20 deg.C,
50 % relative humidity
Mixing chamber
Outdoors
5 deg.C
80 % relative humidity
0.2 m3/s
1 m3/s



 | #1 | #2 | #3
T, deg.C | 5 | 20 | 16.86 (cal.)
RH, % | 80 | 50 | 53.37 (psychart)
V, m3/s | 0.2 | 0.8 | 0.999
, m3/kg | 0.7935 | 0.8402 | 0.83
M, kg/s | 0.252 | 0.952 | 1.204
W, kg/kg | 0.0043 | 0.0073 | 0.0066 (cal.) / 0.0064 (psychart)
h, kJ/kg | 15.859 | 38.545 | 33.796 (cal.) / 33.054 (psychart)
W3 = (M1*W1+M2*W2)/(M1+M2)
h3 = (M1*h1+M2*h2)/(M1+M2)
T3 = (M1*T1+M2*T2)/(M1+M2)

## Slide 159
State 3

## Slide 161: Process
You are designing an evaporative cooling system to ventilate a controlled environment, totally enclosed, poultry house in a hot and dry climate.
Summer design weather conditions for your location are 40 degree C Tdb and 20 % RH.
75 m3/s of outdoor air will be drawn by the evaporative cooling system (75% efficiency) and 15 m3/s of outdoor air will be drawn into the house through infiltration.
The birds in the house are expected to produce 250 kW of total heat of which 40% is latent heat. Determine
    the psychrometric properties of the air mixed by air through evaporative cooling pad and air through infiltration.
    the psychrometric properties of the exhausted air.
    the volumetric flow rate of air exhausted from the house.
    the rate (L/s) at which water must be supplied to the evaporative cooling pads by a water pump. When a (water flow/evaporation rate) ratio of 3 is desire.

## Slide 162
75 m3/s
4
3
1
2
15 m3/s
Evaporative cooler
infiltration
Poultry House

## Slide 163
State 1
State 2
State 3
= 16.66, = 86.3, = 102.96 kg/s
T3 = ( * T1 + * T2) / = 28.69 deg. C
W3 =( * W1 + * W2) / = 0.0137 kg/kg
Zoom out

## Slide 164
= 75 m3/s
2 = 0.8689 m3/kg
= 86.3 kg/s
4
3
1
2
= 15 m3/s
1 = 0. 9003 m3/kg
= 16.66 kg/s
Evaporative cooler
infiltration
Poultry House
T1 = 40 deg. C
RH1 = 20 %
W1 = 0.0092 kg/kg
T2 = 26.51 deg. C
RH2 = 67.1 %
W2 = 0.0146 kg/kg
T3 = 28.69 deg. C
W3 = 0.0137 kg/kg
= 102.96 kg/s
100 kW latent
150 kW sensible heat
T = 150 / ( * Cp) = 150 / (102.96*1.006) = 1.448 deg. C
hfg = 2501 – 2.42 * (28.69+1.448) = 2428 kJ/kg
W= 100 / ( * hfg) = 100 / (102.96 * 2428) = 0.0004 kg/kg
T4 = T3 + T = 28.69 + 1.448 = 30.138 deg. C
W4 = W3 + W = 0.0137 + 0.0004 = 0.0141 kg/kg

## Slide 165: The volumetric flow rate and properties of states 3 and 4
Zoom in to the limit.
State 3
State 4

## Slide 166: the rate (L/s) at which water must be supplied to the cooling pad = 3 * (0.0146 – 0.0092) * 75 / 0.9003 = 1.3495 kg /s

## Slide 167: Reference on Psy. Examples
Albright, L.D. 1990. Chapter 2 – Psychrometrics. Environment Control for Animals and Plants. An ASAE Textbook. ASAE, St. Joseph, MI, USA.